## Sheet1
Error_Code | Possible_Problem | Recommended_Action
Error:212 | The bulb isn't working at night; during nighttime, both current and voltage are zero. | Check if the bulb is functional. Inspect the sensors and battery power to ensure they are in good condition.
Error:111 | The bulb lights up during the daytime, possibly due to a faulty light sensor or incorrect wiring. | Replace the bulb and verify the wiring and sensor functionality.
Error:311 | The solar panel connection might be loose or damaged, causing improper charging. | Check the current sensor and charge controller for possible issues.
Error:312 | For three consecutive days, daytime data shows a drop in power, indicating a possible solar panel issue. | Replace the bulb or consider changing the solar panel if necessary.
Error:313 | For three consecutive days, daytime data shows irregular power readings, suggesting a potential sensor malfunction. | Replace the bulb and inspect the charge controller for faults.
Error:314 | The battery reaches full charge in just 2 hours, which may indicate overcharging or a faulty charge controller. | Check the charge controller to ensure it is regulating the charging process correctly.
Error:305 | The sudden jumps or down of soc values on every hour. | Recalibrate the current sensor or replace it if necessary.
Error:306 | The consecutive 3 days has idle trends in zero of soc during night time. | Check if the area has still good internet connectivity, check the gsm if still working or have a load data, check the microcontroller if still work properly and check the battery if still present.
Error:317 | The consecutive 3 days has idle trends in zero of soc during day time. | Check if the area has still good internet connectivity, check the gsm if still working or have a load data, check the microcontroller if still work properly and check the battery if still present.
Error:308 | The consecutive 3 days has idle trends in 100% of soc during night time. | Check if the bulb is still working or present if not then replace the bulb.
Error:319 | The consecutive 3 days has idle trends in 100% of soc during day time. | Check if the bulb is still working or present if not then replace the bulb.
Error:300 | Discharge very quickly during night time. | Check the battery if still in a good condition if not then replace with a good condition battery.
Error:400 | No present data of all components | Needs overall 'trouble shoot or 'check the microcontroller if still working.